##### National Park Service

U.S. Department of the Interior

Glacier National Park

Montana

Many Glacier/Swiftcurrent Sewage System and Wastewater Treatment Improvements

Finding of No Significant Impact

August 2007

## Finding of No Significant Impact

Many Glacier Sewage System and Wastewater Treatment Improvements

Glacier National Park • Montana

A portion of Waterton-Glacier International Peace Park

Glacier National Park will be making improvements to the sewage system and wastewater treatment facilities for the Swiftcurrent and Many Glacier developed areas. In general, the Many Glacier wastewater treatment plant (WWTP) is providing adequate treatment of the wastewater according to fecal contamination levels measured in waters around the WWTP in 2005 that were found to be below EPA recreational standards. However, the facilities have deteriorated consistent with age and exposure to the relatively harsh environmental conditions. Both the sewage lines and treatment systems are over 30 years old and are showing signs of deterioration. In addition, the Many Glacier WWTP does not currently have a Montana Department of Environmental Quality (MDEQ) discharge permit for groundwater. MDEQ has indicated that a groundwater discharge permit for the WWTP is required for continued operation. The discharge requirements that will be defined in the permit will be based on the water quality standards that MDEQ has adopted. Replacement or rehabilitation of parts, in order to meet the sewage and treatment system permit standards, is described below.

The sewer system includes two lines, one starting at Swiftcurrent and the other in Many Glacier, that merge and flow to the WWTP. The Many Glacier sewage lines, including all pipes running to the main line, were repaired or replaced during rehabilitation of the hotel between 2002 and 2004. According to a recent engineering report, the Swiftcurrent section has experienced recent blockages and some pipes are too narrow to meet MDEQ ground water discharge standards. Additional testing and inspection of these segments and the main line to the WWTP will determine how much of the system will need replacement.

The dry well area which contains the pumps and valves at the Swiftcurrent lift station is considered a confined space. This requires that all WWTP operators obtain confined space training and a refresher course be conducted every 12 months. The categorization also requires at least two operators that are confined space trained be at the facility when repairs are made. The WWTP is already short-staffed and having two people at one location is inefficient and often difficult to schedule. Major modifications to the lift station are recommended to enhance safety and efficiency for operators by eliminating the confined space designation.

The Many Glacier wastewater treatment facility was built in 1975 and is located approximately two miles east of the Many Glacier Hotel. The facility is operated from May to October and consists of the headworks, an aerated lagoon, and percolation ponds. There are deficiencies with the aeration system within the lagoon and the original lagoon liner has been damaged several times by bears that have accessed the lagoon. The lagoon has not been emptied of accumulated solids since its construction, reducing the capacity and efficiency of the lagoon. In addition, the lagoon’s recirculation system is inoperable due to pump failure. The percolation ponds are currently not fenced, they pose a potential human health risk and some people have attempted to fish in them.

There are three problems with the existing fencing that surrounds the WWTP and lagoon: 1) there are several sections that require repair to prevent bears from entering the area, 2) bears can also enter the fenced area by climbing trees adjacent to the fence and climbing over the top of the fence, and 3) its location at the bottom of the berm prevents Facilities Management personnel from mowing the slope of a berm. Mowing, conducted once every summer, is needed to prevent trees and shrubs from becoming established and eventually compromising the berm.

Preferred Alternative

This alternative presents the National Park Service’s preferred alternative and is the proposed undertaking for Section 106 compliance. Under this alternative, the following improvements to the sewage system and wastewater treatment facility will be made:

Gravity Sewers: The sewer pipes coming from the Swiftcurrent developed area, including the Swiftcurrent Ranger Station (Many Glacier) Historic District and Swiftcurrent Auto Camp Historic District, are old clay pipes that require replacement. Pipe replacement will be conducted using a pipe bursting method. This will require digging, with a backhoe, a five foot long trench, approximately three feet wide at each manhole. The old pipe is then burst by slipping a new pipe within it. This method reduces the amount of trenching required as the old and new piping remains in the ground. Approximately 2150 feet of gravity lines will be replaced. Gravity lines coming from the Many Glacier developed area (Many Glacier Hotel Historic District) were replaced during renovations made in 2002-2004 and no additional improvements are required at this time.

Force Mains: The force mains running from both the Swiftcurrent and Many Glacier areas to the WWTP will be inspected at the lift stations. In addition, several three foot sections of pipe will be removed along the line as representative samples for corrosion analysis. Depending on the outcome of this analysis, the force main lines may require replacement. The force main is installed under the road bed of Glacier Route Three (i.e. the main Swiftcurrent/Many Glacier road). If only small sections require replacement, the work would be done by pipe bursting. If the entire main line (approximately 9350 feet) requires replacement, or a large section, it would be done by open trenching along its length.

Lift Stations: At the Swiftcurrent lift station, a vacuum-primed pump package system will be installed. This system eliminates the confined space designation, provides better access for maintaining equipment, and provides standardized pumping equipment throughout the park.

Wastewater Treatment Plant: Approximately 60 percent of the area within the fenced compound of the WWTP will be disturbed. The exact amount would depend on the condition of pipes and equipment. The following improvements will be made:

The initial sewage intake filtering unit in the western channel of the headworks will be replaced with an in-line grinding unit. The liner will be replaced after accumulated solids are removed from the lagoon area. An aeration diffuser system within the lagoon will be replaced and the capacity of the aeration system (including the existing blowers) will be evaluated to provide aeration capacity for additional nitrification. A floating baffle will be provided in the lagoon to create a quiescent zone for settling that would have a hydraulic detention time of one to two days. And the recirculation pump system will be replaced to provide additional flexibility and process reliability to the lagoon.

The existing aeration control system will be replaced in the control building. The effluent flow measurement equipment and an electronic data recorder will be installed along with the replacement of the effluent flow control system. Maintenance of the control building includes resealing/replacing the roof, replacing the concrete sidewalks around the building and replacing the steel access hatch with an aluminum hydraulic assisted hatch.

All percolation ponds’ levees will be surveyed for leaks and repaired as needed. A cover hatch will be installed over the pond distribution box. The drain pipes through the berms of ponds Nos. 1, 3, and 4 will be removed or plugged. And percolation ponds No. 3 and 4 will be cleaned by dredging.

The existing chain link fence around the WWTP and lagoon will be removed from the bottom of the lagoon berm and a new chain link fence that has been dipped in green vinyl to reduce the visual intrusion, will be installed in the best location for maintenance and to discourage bear entry; this may be along the top of the berm. Two solar-powered electrical strands will be added to the fence to further discourage bears from entering. A wood split rail fence or other aesthetically appealing boundary system will be installed adjacent to the road in front of the percolation ponds to discourage use of the area by the public.

Because this work will require that the sewage system be shut down at both Many Glacier and Swiftcurrent, the work will be conducted before and after the visitor season. The primary work will occur from late March to mid-May and again from September to late December, weather permitting. Some minor work (e.g. fencing, concrete flatwork, and control building renovation) that does not interrupt the flow or treatment of wastewater or visitor access could be conducted during summer months. The work will be conducted in phases starting in 2008 and take approximately 4-5 years. The park has currently budgeted $1.5 million dollars for these improvements.

To mitigate the affects of this project: the following actions will be taken as part of the preferred alternative:

All construction will be limited to a designated area required to complete the work; all activity, including vehicle and material and material use and storage will not be allowed outside predetermined, marked construction/staging zones.

Construction zones will be identified and fenced with construction tape or similar material prior to any construction activity beginning.

All earth moving equipment including haul vehicles will be thoroughly cleaned of mud and weed seed prior to entering the park.

If fuels and hazardous materials are used, a spill protection plan will be approved by the Park Safety Officer.

Soil erosion will be minimized by appropriate erosion control measures. Only certified weed-seed free erosion control materials (e.g. straw or coir bales) will be permitted as erosion control or siltation devices to reduce probability of weed contamination. In addition, coconut silt rolls and fabric silt fences will be allowed depending on site constraints.

Excavated soil may be used in the construction project; excess soil will be stored in approved areas. Topsoil will be removed and conserved separately, then placed back on top after work is completed.

Where trenching occurs, the surface o f the trench will be left adequately mounded to allow for ground settling along the line. Park inspection of all fill, gravel or soil materials into Glacier will be conducted.

Disturbed areas will be promptly revegetated with native species to reduce erosion potential and hasten recovery of soils. In accordance with Glacier’s genetic guidelines, only seeds and plants originating from the park will be allowed in restoration activities. All revegetation efforts will be in accordance with the park’s Road Maintenance Guidelines (NPS 2005).

Initial ground disturbing activities will be monitored by an archeologist. A decision to continue monitoring will be made based upon examination of soils. If during construction previously undiscovered archeological resources are discovered, all work in the immediate vicinity of the discovery will be halted until the resources can be identified and documented and an appropriate mitigation strategy developed in consultation with the State Historic Preservation Officer.

All work will be conducted during daylight hours and workers will commute to and from the site each day and be confined to the day’s work area.

If the golden eagle nest on Mt. Altyn is active, construction within the 800 m- buffer area (Figure 2 from the EA) will be limited to one hour after sunrise and one hour before sunset between April 1 and August 15. If work is conducted during March and April near Swiftcurrent Creek at the WWTP, restrictions on time of day (i.e. no work until one hour after sunrise or one hour before sunset) will be necessary to allow eagles to forage in these areas.

The presence of a park law enforcement ranger and biological technician will ensure compliance with park regulations and enforcement of garbage and food-storage regulations to minimize the risk of habituation or mortality of wildlife. If garbage cans are needed, certified bear-proof containers will be required.

Table 1 summarizes how the two alternatives that were analyzed meet the defined objectives of this project.

Table 1. Summary comparison of alternatives analyzed in this document.

| Objective | No Action Alternative | ##### Preferred Alternative |
| --- | --- | --- |
| Replace aging and deteriorating sewage pipes | Sewer lines would continue to fail and be replaced on an as needed basis. | All sewer lines older than 10 years will be replaced and/or tested to determine their level of deterioration. |
| Make changes to sewage system to meet the standards for a MDEQ groundwater discharge permit | Some of the sewer lines are, and would remain, too small to meet MDEQ standards. | All sewer lines that do not meet MDEQ standards will be replaced and upgraded to meet standards. |
| Modify the Swiftcurrent lift station to eliminate the confined space designation | The Swiftcurrent lift station would remain a confined space and require two employees be present when working at the site. | A new vacuum-primed pump package system will be installed. This system eliminates the confined space designation, provides better access for maintaining equipment, and provides standardized pumping equipment installed throughout the park. |
| Repair deficiencies with aeration system at WWTP and provide a quiescent zone prior to the discharge point | Only 2 of the 12 static tube aerators are currently working and there is no quiescent zone prior to the discharge point. | New equipment will solve these deficiencies including a new filtering system, floating aeration diffuser system, and floating baffle divider. |
| Replace the original lagoon liner that has been damaged several times | The current liner would not be replaced and may leak into surrounding soils. | The liner will be removed and replaced with a new liner. |
| Remove accumulated solids from the lagoon. | The lagoon would not be emptied of accumulated solids. | The lagoon will be emptied of accumulated solids. |
| Replace inoperable recirculation system pump at lagoon | The lagoon recirculation system is no longer functioning due to pump failure. It would not be replaced. | The recirculation pump system in the lagoon will be replaced to provide additional flexibility and process reliability. |
| Fence the percolation ponds to reduce a potential human health risk | No new fencing would be installed around the percolation ponds. | A wood split rail fence or other aesthetically appealing boundary system will be installed adjacent to the road in front of the percolation ponds to discourage use of the area by the public. |
| Replace and move the existing fence around the lagoon | The current fence would remain in place. Because of its location it can be crossed by bears climbing trees adjacent to the fence and its location at the bottom of the berm prevents Facilities Management personnel from mowing the slope of the berm. | A new chain link fence dipped in green vinyl will be installed, possibly on the top of the berm, where bears could not breach it and where the slope of the berm will be accessible for mowing. |
| Does the alternative meet project objectives? | No | Yes |

Alternatives Considered But Eliminated

Performing all the construction work and disturbance in the summer season was considered but rejected. While this would have avoided disturbance to wildlife in the shoulder season, it would have required closing most of the visitor services provided at Many Glacier and Swiftcurrent including the hotels and campground. Traffic delays on the road would also occur because of the amount of trenching that is required. Closing the facilities for an entire summer and traffic delays in conjunction with work on the GTSR resulted in this option being eliminated from further consideration.

Environmentally Preferred Alternative

The environmentally preferred alternative is determined by applying the criteria suggested in the National Environmental Policy Act of 1969 (NEPA), which is guided by the Council on Environmental Quality (CEQ). The CEQ provides direction that the “environmentally preferable alternative is the alternative that will promote the national environmental policy as expressed in NEPA Section 101”:

- fulfill the responsibilities of each generation as trustee of the environment for succeeding generations;

- assure for all generations safe, healthful, productive, and esthetically and culturally pleasing surroundings;

- attain the widest range of beneficial uses of the environment without degradation, risk of health or safety, or other undesirable and unintended consequences;

- preserve important historic, cultural and natural aspects of our national heritage and maintain, wherever possible, an environment that supports diversity and variety of individual choice;

- achieve a balance between population and resource use that will permit high standards of living and a wide sharing of life’s amenities; and

- enhance the quality of renewable resources and approach the maximum attainable recycling of depletable resources.

The Preferred Alternative fulfills all six criteria better than the No Action Alternative. The Preferred Alternative accomplishes criteria 1, 2, and 3 by eliminating sewage pollution, or the threat of pollution, into the soils, groundwater, and nearby streams. Criteria 2 and 4 are fulfilled by providing long-term maintenance solutions and by protecting the historic districts. The proposed improvements to the sewer system will provide a system better equipped to handle the volume of sewage produced in the area, thus fulfilling criteria 5. The No Action Alternative does not fulfill any of the criteria because the chance of sewage leaks into the surroundings and sewage backups into historic buildings would remain. Neither alternative addresses criteria 6. Therefore, the Preferred Alternative is the environmentally preferred alternative.

#### Why the Preferred Alternative Will Not Have a Significant Effect on the Human Environment

As defined in 40 CFR Section 1508.27, significance is determined by examining the following criteria:

Impacts that may be both beneficial and adverse

The Preferred Alternative will result in moderate short-term local adverse impacts to wildlife due to noise and human presence during construction. The cumulative effects will be moderate long-term local adverse due to the proposed project and ongoing Many Glacier Hotel rehabilitation work. Mitigation measures proposed will provide the presence of a park ranger and biological technician while construction is underway, to ensure compliance with park regulations and enforcement of garbage and food storage regulations. This will minimize the risk of wildlife habituation or mortality. If garbage cans are needed, certified bear-proof garbage container will be required. Impacts to soils will be minor, short term local and adverse due to excavation activities. Impacts to grizzly bears, Canada lynx will be minor short term local and adverse due to noise and human presence. Impacts to gray wolves will be negligible, short term local and adverse due to noise and human presence. Impacts to bald eagles will be negligible, long term, local and beneficial due to the reduction in potential for water contamination. Impacts to bull trout will be negligible long term local and beneficial due to the reduction in potential for water contamination. For other state listed species of concern, impacts will be minor, short term local and adverse due to noise and human presence. There will be moderate long term local beneficial impacts to water quality due to the reduction in potential for leaks fro the pipes. There will be moderate long term local and beneficial impacts on park operations due to the elimination of the “confined” space and improved access to the lagoon.

Degree of effect on public health or safety

The actions proposed under the Preferred Alternative represent the recommendations from the preliminary engineering report for the wastewater treatment system and will meet the requirements for a MDEQ discharge permit. Effects on public health and safety will be improved with the improvements to the wastewater treatment system, because of reduced chance for contamination.

Unique characteristics of the geographic area such as proximity to historic or cultural resources, park land, prime farm lands, wetlands, wild and scenic rivers, or ecologically critical areas

The proposed project will be conducted to benefit and support visitor services in two historic districts and will not affect a floodplain.  No wetlands will be affected by actions proposed in either alternative according to the USFWS (1992) National Wetland Inventory Mapping. The area provides year round habitat for all of Glacier’s ungulate species and the drainage contains critical winter and spring range for bighorn sheep as well as important lambing and rutting grounds. Most of the park’s large carnivores are also found here. While many of these species avoid the area in the summer when visitors and employees are present, the do occupy the area during the late fall, winter and early spring due to the remoteness and relative lack of human activity.

Degree to which effects on the quality of the human environment are likely to be highly controversial

None

Degree to which effects on the quality of the human environment is highly uncertain or involves unique or unknown risks

Implementing the projects mitigation measures and protocols decreases the highly uncertain or unique or unknown risks which affect the quality of the human environment.

Degree to which the action may establish a precedent for future actions with significant effects or represents a decision in principle about a future consideration

None.

Whether the action is related to other actions with individually insignificant but cumulatively significant impacts

This action does not significantly add to cumulative impacts from other actions.

Degree to which the action may adversely affect districts, sites, highways, structures, or objects listed on the National Register of Historic Places or may cause loss or destruction of significant scientific, cultural, or historical resources

The findings of previous archeological surveys document that there are archeological resources in undisturbed ground in the project vicinity. However, as planned the excavation work proposed under this alternative will occur in ground previously disturbed, both horizontally and vertically, by past utility construction activities. Consequently, archeological resources are not expected to be encountered during digging for this project. The park’s cultural resource specialist consulted with the Blackfeet Tribal Historic Preservation Officer and the Confederated Salish and Kootenai Tribal Historic Preservation Department regarding this project. It was agreed that an archeologist will resurvey the areas proposed for disturbance and will monitor initial ground-disturbing activities. A decision to continue monitoring will be made based upon examination of soils. Should artifacts be identified during the project, work will cease in the immediate area and the park’s cultural resource specialist will be notified. Additional consultation in accordance with 36 CFR 800.13 for post-review discoveries will occur. Operations will not presume until an appropriate mitigation strategy is developed in consultation with the State Historic Preservation Officer. Based upon current knowledge, the impacts to archeological resources from the Preferred Alternative will be negligible long-term site-specific adverse. Under Section 106 the park has determined that no historic properties will be affected.

Degree to which the action may adversely affect an endangered or threatened species or its critical habitat

Impacts from the Preferred Alternative will be negligible short-term local and adverse for the gray wolf and bald eagle, minor short-term local and adverse on grizzly bears and Canada lynx, negligible long-term local and beneficial to bull trout, minor short-term local and adverse on species of concern, and there will be no effect on federally listed plant species. Cumulative impacts in conjunction with the Preferred Alternative will be moderate long-term local adverse and will result primarily from extending shoulder season work for an additional four years. Glacier National Park biologists have determined that this project may affect but is not likely to adversely affect the Canada lynx and grizzly bear and prepared a Biological Assessment (BA) in accordance with Section 7 of the Endangered Species Act. The US Fish and Wildlife Service concurred with the BA on July 23  2007.

Mitigation measures proposed will limit work hours to daylight hours and workers will commute to and from the site each day and be confined to the day’s work area. The presence of a park ranger and biological technician on the site will ensure compliance with park regulations and enforcement of garbage and food storage regulations. This will minimize the risk of wildlife habituation or mortality. If garbage cans are needed, certified bear-proof garbage container will be required. Disturbed areas will be promptly revegetated with native species to reduce erosion potential and hasten recovery of soils.

Whether the action threatens a violation of federal, state, or local environmental protection law

The action does not threaten any federal, state, or local environmental protection laws or regulations.

Impairment

In addition to reviewing the list of significance criteria, the National Park Service has determined that implementation of the proposal will not constitute an impairment to Glacier National Park’s resources and values. This conclusion is based on a thorough analysis of the environmental impacts described in the Many Glacier/Swiftcurrent Sewage System and Wastewater Treatment Improvements Environmental Assessment, the public comments received, and the professional judgment of the decision maker guided by the direction in NPS Management Policies (NPS 2006). Although the project has some negative impacts, in all cases these adverse impacts are the result of actions taken to preserve and restore park resources and values. Overall, the project results in benefits to park resources and values, opportunities for visitor enjoyment, and it does not result in their impairment.

Public Involvement

Glacier National Park conducted both internal scoping with appropriate National Park Service (NPS) staff and external scoping with the public and interested and affected groups and agencies.

The interdisciplinary process of internal scoping defined the purpose and need for the project, identified potential alternatives to address these needs, determined what the issues were and what resources would be affected and identified the relationship, if any, of the proposed action to other planning efforts at the park.

Public scoping began with letters announcing the project and a press release issued on June 30, 2006. Letters were sent to the park’s mailing list for EAs, which included various federal, state, and local agencies, such as the U.S. Fish and Wildlife Service (USFWS) and the Blackfeet Tribal Business Council, and the Confederated Salish and Kootenai Tribes. The announcement was also posted on the National Park Service’s public comment website.

In accordance with 36CFR800.8(c), Glacier National Park also notified the Montana State Historic Preservation Officer and the Advisory Council on Historic Preservation that it intended to prepare a combined Environmental Assessment/Finding of Effect for the proposed project.

Six comments were received during scoping for this project. The Alberta Minister of Environment had no concerns with the project. Both the Blackfeet Tribal Historic Preservation Office and the Salish and Kootenai Tribal Preservation Office requested further consultation on the project. The Advisory Council on Historic Preservation (ACHP) had no comments but recommended that we continue to consult with the Montana State Historic Preservation Office and local tribes. One respondent requested additional information on the location and type of upgrades to be done. These were presented in this EA. A sixth respondent thought the project was worthwhile.

The EA was provided to the public for a 30 day review on July 12, 2007. The announcement was also posted on the National Park Service’s public comment website.

Four comments were received on the EA.  The US Fish and Wildlife Service concurred with the determinations found in the Biological Assessment. Glacier Park Boat Co. requested a connection between the Boat Company housing area and the Many Glacier sewage system be considered. This was considered and determined that the connection would run along the road through an already disturbed area and would qualify for a categorical exclusion if and when the Boat Company was ready to hook into the system. The Advisory Council on Historic Preservation (ACHP) had no comments but recommended we continue to consult with the Montana State Historic Preservation Office and local tribes. And the forth respondent thought the preferred alternative better met the project’s purpose and need.

A press release will be issued announcing the availability of the FONSI. A copy will be sent to all commenters, and it will be placed on the NPS public web site.

Conclusion

The preferred alternative does not constitute an action that normally requires preparation of an environmental impact statement (EIS).  The preferred alternative will not have a significant effect on the human environment. Unmitigated negative environmental impacts that could occur are minor or less in degree.  There are no unmitigated adverse impacts on public health, public safety, threatened or endangered species, sites or districts listed in or eligible for listing in the National Register of Historic Places, or other unique characteristics of the region.  No highly uncertain or controversial impacts, unique or unknown risks, significant cumulative effects, or elements of precedence were identified. Consultation in accordance with Section 106 of the National Historic Preservation Act will be completed with the State Historic Preservation Officer, the Blackfeet Tribal Historic Preservation Officer, and the Confederated Salish and Kootenai Tribal Historic Preservation Department when construction documents are available for review, and prior to the start of construction.  The US Fish and Wildlife Service concurred with the determination of effect in the BA on July 23, 2007. Therefore consultation under Section 7 of the Endangered Species Act is concluded. Implementation of the action will not violate any federal, state, or local environmental protection laws.

The action will not result in major, adverse impacts to a resource or value whose conservation is (1) necessary to fulfill specific purposes identified in the establishing legislation and proclamation of Glacier National Park; (2) key to the natural or cultural integrity of the park; or (3) identified as a goal in the park’s general management plan or other relevant National Park Service planning documents, there will be no impairment of the park’s resources or values.

Based on the foregoing, it has been determined that an EIS is not required for this project and thus will not be prepared.

Recommended: /s/ Michael O. Holm		8/28/2007

Michael O. Holm    	Date

Superintendent, Glacier National Park

Approved:  /s/__Anthony J. Schetzsle      ___9/4/2007__________

Snyder 	Date

Director, Intermountain Region